IED_DOC_CONFIGURATOR  v 0.0.2 — user manual

Source code of the program: OMICRON_CONFIGURATION_FOR_IED

1. About

This program was created as an attempt to automate part of the work on preparing and directly carrying out tests at a substation.

It is essentially an MVP (minimum viable product) for a future project. It is not a finished product, so there may be inaccuracies. Always check the created files in OMICRON Test Universe before using them on site.

The program takes the data of a General_PB (Excel) project and the CID files and creates files for OMICRON Test Universe. What General_PB is: IEC61850_text_configurator

• hardware configuration (*.ohc) — names of binary inputs/outputs, analog channels and the Sampled Values (SV) streams;

• GOOSE configuration (*.xml) — GOOSE subscriptions and simulations mapped to the CMC inputs/outputs;

• update of existing GOOSE configurations from new CID files.

The program only reads the Excel and CID files and never changes them.

2. Requirements

Start: the exe file IED_DOC_CONFIGURATOR (nothing to install) or from PyCharm / Python: ied_doc_configurator.py. Next to it: omicron_configuration.py, omicron_goose_config.py and ied_doc_manual.py; the package openpyxl is needed.

Project folder:

<Project>\

General_PB.xlsm          main workbook of the project

DOC\                     device files <IED>.xlsm

Library\                 master files:

default_01.ohc        master of the hardware configuration

default_goose.xml     master of the GOOSE configuration

CID\                     CID files (*.cid, *.icd, *.scd, *.iid) of all devices taking part in GOOSE

Omicron\                 CREATED BY THE PROGRAM — results

<IED>\                one folder per device

The master files are empty configurations saved in Test Universe. The program does not build them from scratch, it fills them:

• default_01.ohc — with the GOOSE virtual inputs/outputs enabled (7×24) and three SV streams (6 groups of 4 analog channels);

• default_goose.xml — an empty configuration of the GOOSE module.

General settings (CMC, PTP, IRIG-B, network port etc.) are set once in the master and go into every created file.

3. Main window

Title             name and version of the program

Button  i         this manual (choose the language at the top of the panel)

Project folder    path of the project folder

Browse...         choose the project folder; the last folder is remembered

Create Omicron_configurations   — section 4

Create GOOSE_configurations     — section 5

Update GOOSE_configurations     — section 6

Open Omicron folder             — section 7

Log               progress and the final report of every action

Status line       Ready / Working… / result / Stopped

While an action runs the buttons are disabled and the window stays open (the log can be scrolled). A message appears at the end.

4. Create Omicron_configurations (*.ohc files)

What it does: for every selected device it creates a Test Universe hardware configuration — names of binary inputs and outputs, names of the SV analog channels and the parameters of the SV streams.

Steps:

1. Set the project folder.

2. Press the button — the list of devices (files DOC\*.xlsm) with check boxes appears; buttons Select all / None.

3. If Library has several *.ohc files, a master choice appears above the list.

4. Tick the devices and press Create (Cancel — abort).

Where the data come from (device file DOC\<IED>.xlsm):

• "Omicron Binary Inputs": A — channel (Bin. in 1…12, vBin. in 1-1 … 7-24), D — Omicron ID → name of the CMC binary input;

• "Omicron Binary Outputs": A — channel (Bin. out 1…8, vBin. out 1-1 … 7-24), D — Omicron ID → name of the CMC binary output;

• "Omicron AI <test>" (Test 1, Test 2, …): A — channel, D — Omicron ID → analog channel name, F — SV ID → stream of the group:

V L1, V L2, V L3, V E      → SV Voltage 1      I L1 … I E      → SV Current 1

V(2)-1 … V(2)-E           → SV Voltage 2      I(2)-1 … I(2)-E → SV Current 2

V(3)-1 … V(3)-E           → SV Voltage 3      I(3)-1 … I(3)-E → SV Current 3

(group n = SV stream n)

Empty Omicron ID → the channel keeps the name of the master ("vBin. in 1-2", "V(2)-1" …).

SV streams (from General_PB, sheet SV, by SV ID) — in the Test Universe dialog "Configure Sampled Values", tab Stream n:

svID, Destination MAC, APPID, VLAN ID, VLAN priority     — from the sheet SV

Dataset reference        = IEDName + Dataset   (MU01_QW1GMU01/LLN0$PhsMeas1)

Control block reference  = IEDName + LD/LLN0$MS$MSVCB0<LD number>

ConfRev = 1, port ETH1

The Dataset Mapping is filled too — which CMC channel goes into which attribute of the data set. Attribute captions (MU01.TCTR1.AmpSv…) and the line "Select IED / Sampled Values ID" stay from the master. A stream without SV ID stays as in the master.

Result:

Omicron\<IED>\<IED>_Omicron_AI_Test_<n>.ohc   — one file per sheet "Omicron AI …" with data

Omicron\<IED>\<IED>_Omicron.ohc               — when there is no SV data (GOOSE only)

Omicron\_omicron_report.txt                   — report

A device without Omicron data is skipped (a line in the report). The binary inputs/outputs are the same in all tests of a device.

The report warns about: SV ID not on the sheet SV of General_PB; two different SV IDs in one group V(n) / I(n); names with characters that are not allowed (A-Z a-z 0-9 _, first character a letter); channels of the sheet that the master does not have.

5. Create GOOSE_configurations (*_GOOSE.xml files)

What it does: for every selected device it creates a configuration of the Test Universe GOOSE module:

• Subscriptions (the CMC RECEIVES the GOOSE of the device) — sheet "Omicron Binary Inputs": every GCB of the device on this sheet;

• Simulations (the CMC PUBLISHES GOOSE instead of other devices) — sheet "Omicron Binary Outputs": every publisher GCB (columns E — IED Name, F — GCB Name).

Steps:

1. Put the CID of the device and of all publishers it subscribes to into the CID folder of the project.

2. Press the button, tick the devices, press Create.

Where the data come from:

• from the CID: MAC, APPID, GoID, GCB and data set references, VLAN ID and priority, ConfRev, MinTime/MaxTime (repetition Initial/Final) and the WHOLE data set (stVal and quality .q);

• from the device file: which signals go to which CMC inputs/outputs — column B (ELEMENT) is the signal, column A the channel:

Bin. in n / Bin. out n              → CMC input/output n

vBin. in g-k / vBin. out g-k        → 24 + (g−1)·24 + k    (1-3 → 27, 7-24 → 192)

A GCB is found in the CID files by its MAC address (from the sheet or from General_PB, sheet GEN), so the IED name inside the CID may differ from the project name.

CID check: if any needed GCB has no CID file, the program writes NOTHING and lists the missing ones, for example:

CID files are missing in …\CID

W1G_D60: MU02_QC1G / GCB VT (MAC 01-0C-CD-01-00-64) - no CID file with this GCB

Add the files and run again.

Result: Omicron\<IED>\<IED>_GOOSE.xml and Omicron\_goose_report.txt. The report also shows differences General_PB ↔ CID (GoID, APPID, VLAN) — the file gets the CID value, i.e. the real value of the device; and signals of the sheet that are not in the CID data set.

Limits of this version: Boolean signals and quality (.q) are supported. A GCB with other types (Dbpos, INT, FLOAT, Timestamp) is skipped with a note in the report.

6. Update GOOSE_configurations (from new CID files)

Why: a device was reconfigured — signals were added, removed or moved in a GCB, MAC, APPID, VLAN or ConfRev changed. The button updates an existing *_GOOSE.xml and keeps your manual work in Test Universe, so nothing has to be re-entered by hand.

Steps:

1. Press the button — the "Open files" dialog appears; choose one or more *_GOOSE.xml (Ctrl / Shift).

2. Choose the folder with the NEW CID files (only the changed ones are enough).

Both folders are remembered.

How each GCB block is updated: the GCB is searched in the new CID files by its reference (IED + LD + GCB name), else by MAC.

Found:       from the CID — MAC, APPID, GoID, references, VLAN, ConfRev, Initial/Final, signals and their order;

from the XML — Enable, SimulateFlag, Multiplier and every CMC mapping (number, Bit, Value, Inverted)

signal still there      → mapping kept

signal added            → added without a mapping

signal removed          → removed, report "mapping … lost"

signal type changed     → mapping removed (in the report)

signals moved           → order as in the CID, the mappings move with their signals

CID of the device present, GCB not   → block removed ("GCB removed")

no CID of the device in the folder   → block unchanged ("no CID for this device, left unchanged")

A renamed signal (Ind053 → Ind056) looks like "removed + added" — map it again. New signals are NOT put on free inputs automatically.

Result: next to the original — <IED>_GOOSE_updated_<date>_<time>.xml (the original is not changed). The file is written only when something changed; otherwise the report says "nothing to update". Report _goose_update_report_<date>_<time>.txt — in the same folder and in the log.

Excel and General_PB are not changed. If a data set changed, update it in General_PB too.

7. Open Omicron folder

Opens the folder <Project>\Omicron in Explorer. If it does not exist yet, the program says so.

8. Typical messages and what to do

Project folder not found / General_PB.xlsm not found  → choose the folder with General_PB.xlsm and DOC

No master .ohc file / Master file not found           → put default_01.ohc or default_goose.xml into Library

Folder with the CID files not found                   → create the folder CID in the project

CID files are missing …                               → add the CID files of the listed devices (section 5)

SV ID … not on General_PB SV                          → the SV ID of the test sheet is not in General_PB; the stream stays as in the master

data type(s) … not supported yet                      → the data set has a type that is not supported yet (section 5)

not read - …                                          → the file is damaged or cannot be read

A file open in Excel is read from a temporary copy — Excel does not have to be closed.